## Sheet1
CODE | R1 | S2 | G3 | ADDR | RTP | DESC1 | DESC2 | DESC3 | DESC4 | DESC5 | VOLTAGE | D1TAG | D1DESC | D1BLK | D1LOC | D2TAG | D2DESC | D2BLK | D2LOC | D3TAG | D3DESC | D3BLK | D3LOC | D4TAG | D4DESC | D4BLK | D4LOC | D5TAG | D5DESC | D5BLK | D5LOC | D6TAG | D6DESC | D6BLK | D6LOC
1771-IAD | 1 | 2 | 0 | I:002/00 | TB20 | BANK #1 FIBER | WASTE REMOVAL BLOWER | START HS100BR | REMOTE |  | 120VAC INPUTS | TB1 |  | HT0001 | JBOX1 | HS100BR | CYCLE¦START | HPB11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/01 |  | BANK #1 FIBER | WASTE REMOVAL BLOWER | STOP HS100BS |  |  |  | TB1 |  | HT0001 | JBOX1 | HS100BS | STOP | HPB11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/02 |  | BANK #2 FIBER | WASTE REMOVAL BLOWER | START HS1001BR | REMOTE |  |  | TB1 |  | HT0001 | JBOX1 | HS1001BR | START | HPB11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/03 |  | BANK #2 FIBER | WASTE REMOVAL BLOWER | STOP HS1001BS |  |  |  | TB1 |  | HT0001 | JBOX1 | HS1001BS | STOP | HTS11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/04 |  | TUB OUTLET TEMPERATURE | NOT LOW(ALARM) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D568TS | TUB OUTLET¦TEMP | HTS12 | FIELD | TB1 |  | HT0001 | JBOX1 | D569TS | TUB OUTLET¦TEMP | HTS12 | FIELD | D570TS | TUB OUTLET¦TEMP | HTS12 | FIELD | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/05 |  | TUB INLET TO HEATER FLOW | NOT LOW (TRIP) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D2150FS | TUB INLET | HFS11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/06 |  | SPARE
|  |  |  | I:002/07 |  | COMBUSTION BLOWER | RUNNING |  |  |  |  | TB1 |  | HT0001 | JBOX1 | MS101 |  | HMS21 | MCC | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/10 |  | INSTRUMENT AIR PRESSURE | NOT LOW (IPS) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D006PS | AIR PRESS OKAY | HPS11 | CAB5 | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/11 |  | AIR DAMPER | AT HIGH FIRE (>80%)(PFS) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D003WS2 | HIGH FIRE | HLS11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/12 |  | AIR DAMPER | AT LOW FIRE (<20%)(LFS) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D003WS1 | LOW FIRE | HLS11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/13 |  | PURGE AIR FLOW | NOT LOW (PAS) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D581FS | PURGE OKAY | HFS11 | CAB5 | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/14 |  | COMBUSTION AIR PRESSURE | NOT LOW (AS) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D582PS | COMB AIR¦OKAY | HPS11 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | I:002/15 |  | SPARE
|  |  |  | I:002/16 |  | STACK TEMPERATURE | NOT HIGH |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D004TS | STACK TEMP | HTS12 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
|  |  |  | SPACER | [19 empty] | CR-MAN | MANUAL¦OVERRIDE | HCR22 | PNL3
|  |  |  | I:002/17 |  | STEAM PRESSURE | NOT LOW (>20PSIG) |  |  |  |  | TB1 |  | HT0001 | JBOX1 |  | STEAM PRESS | HPS12 | FIELD | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB2 |  | HT0003 | CAB5
1771-IAD | 1 | 2 | 1 | I:003/00 | TB21 | FLAME DETECTED NO.1 |  |  |  |  | 120VAC INPUTS | TB1 |  | HT0001 | JBOX1 | D576WT1 | FLAME No. 1 | HTS11 | FIELD
|  |  |  | I:003/01 |  | FLAME DETECTED NO.2 | [5 empty] | TB1 |  | HT0001 | JBOX1 | D576WT2 | FLAME No. 2 | HTS11 | FIELD
|  |  |  | I:003/02 |  | SPARE
|  |  |  | I:003/03 |  | LEAK TEST
|  |  |  | I:003/04 |  | HEATER RESET
|  |  |  | I:003/05 |  | STOP HEATER | [5 empty] | TB1 |  | HT0001 | JBOX1 | 434PB | HEATER STOP | HPB11 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:003/06 |  | EMERGENCY STOP | [5 empty] | TB1 |  | HT0001 | JBOX1 | 226PB | EM STOP | HPB12M | CAB5 | TB1 |  | HT0001 | JBOX1 | 226PBA |  | HPB12M | CAB5
|  |  |  | I:003/07 |  | START HEATER | [5 empty] | TB1 |  | HT0001 | JBOX1 | 436PB | HEATER START | HPB11 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:003/10 |  | ALARM ACKNOWLEDGE | [5 empty] | TB1 |  | HT0001 | JBOX1 | 437PB | SILENCE | HPB11 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:003/11 |  | LAMP TEST | [5 empty] | TB1 |  | HT0001 | JBOX1 | 438PB | LAMP TEST | HPB11 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:003/12 |  | WATCHDOG OPERATING | [5 empty] | TB1 |  | HT0001 | JBOX1 | 1020CR | WATCHDOG¦TIMER | HCR21 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:003/13 |  | SPARE
|  |  |  | I:003/14 |  | TRIP STRING
|  |  |  | I:003/15 |  | SAFETY SHUTDOWN
|  |  |  | I:003/16 |  | SPARE
|  |  |  | I:003/17 |  | SPARE
1771-IAD | 1 | 3 | 0 | I:004/00 | TB30 | SPARE |  |  |  |  | 120VAC INPUTS
|  |  |  | I:004/01 |  | GAS FCV AT LOW FIRE | POSITION (LFST) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D008WSC | LOW FIRE | HLS11 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:004/02 |  | GAS PRESSURE | NOT LOW (LPG) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D2000PS | GAS ABOVE MIN | HPS11 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:004/03 |  | GAS PRESSURE | NOT HIGH (HGP) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D2002PS | GAS BELOW MAX | HPS12 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:004/04 |  | UPSTREAM GAS VALVE | CLOSED
|  |  |  | I:004/05 |  | DOWNSTREAM GAS VALVE | CLOSED |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D2001LS | CLOSED | HLS11 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:004/06 |  | SPARE
|  |  |  | I:004/07 |  | SPARE
|  |  |  | I:004/10 |  | SPARE
|  |  |  | I:004/11 |  | SPARE
|  |  |  | I:004/12 |  | SPARE
|  |  |  | I:004/13 |  | OUTPUT MONITOR - | IGNITION TRANSFORMER |  |  |  |  | TB1 |  | HT0002 | JBOX2 | REM01 | IGNITION¦XFMR | HCR21 | CAB5 | TB1 |  | HT0002 | JBOX2
|  |  |  | I:004/14 |  | OUTPUT MONITOR - | PILOT GAS VALVES |  |  |  |  | TB1 |  | HT0002 | JBOX2 | REM02 | PILOT GAS SV | HCR21 | CAB5 | TB1 |  | HT0002 | JBOX2
|  |  |  | I:004/15 |  | OUTPUT MONITOR - | UPSTREAM GAS SHUTOFF VALVE |  |  |  |  | TB1 |  | HT0002 | JBOX2 | REM03 | USTREAM¦SHUT-OFF | HCR21 | CAB5 | TB1 |  | HT0002 | JBOX2
|  |  |  | I:004/16 |  | OUTPUT MONITOR - | DOWNSTREAM GAS SHUTOFF VALVE |  |  |  |  | TB1 |  | HT0002 | JBOX2 | REM04 |  | HCR21 | CAB5 | TB1 |  | HT0002 | JBOX2
|  |  |  | I:004/17 |  | FUSE MONITOR - | GAS VENT VALVE |  |  |  |  | TB1 |  | HT0002 | JBOX2 | REM05 |  | HCR21 | CAB5 | TB1 |  | HT0002 | JBOX2
1771-OAD/B | 1 | 3 | 1 | O:007/00 | TB31 | GAS VENT VALVE (VGV) |  |  |  |  | 120VAC OUTPUTS | TB1 |  | HT0001 | JBOX1 | SV-VGV |  | HSV1 | FIELD | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 | TB2 |  | HT0004 | JBOX2 | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/01 |  | SPARE
|  |  |  | O:007/02 |  | SPARE
|  |  |  | O:007/03 |  | PURGE COMPLETE | [5 empty] | TB1 |  | HT0001 | JBOX1 | 102LT |  | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/04 |  | PURGE ON | [5 empty] | TB1 |  | HT0001 | JBOX1 | 103LT |  | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/05 |  | PILOT ON | [5 empty] | TB1 |  | HT0001 | JBOX1 | 104LT |  | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/06 |  | MAIN ON | [5 empty] | TB1 |  | HT0001 | JBOX1 | 105LT |  | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/07 |  | MAIN READY | [5 empty] | TB1 |  | HT0001 | JBOX1 | 106LT |  | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/10 |  | NO FLAME | [5 empty] | TB1 |  | HT0001 | JBOX1 |  |  | HLT1R | CAB5 | TB1 |  | HT0001 | JBOX1 | TB3 |  | HT0003 | JBOX5 |  |  |  |  | TB4 |  | HT0001 | JBOX6
|  |  |  | O:007/11 |  | SPARE
|  |  |  | O:007/12 |  | SPARE
|  |  |  | O:007/13 |  | SPARE
|  |  |  | O:007/14 |  | SPARE
|  |  |  | O:007/15 |  | AUDIBLE ALARM RELAY | [5 empty] | TB1 |  | HT0001 | JBOX1 | 642CR |  | HCR1 | CAB5 | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB4 |  | HT0001 | JBOX5
|  |  |  | O:007/16 |  | PURGE COMPLETE RELAY | [5 empty] | TB1 |  | HT0001 | JBOX1 | 643CR |  | HCR1 | CAB5 | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB4 |  | HT0001 | JBOX5
|  |  |  | O:007/17 |  | INPUT TEST VOLTAGE | [5 empty] | TB1 |  | HT0001 | JBOX1 | 644CR |  | HCR1 | CAB5 | TB1 |  | HT0001 | JBOX1 | [8 empty] | TB4 |  | HT0001 | JBOX5
1771-OAD/B | 1 | 4 | 0 | O:010/00 | TB40 | IGNITION TRANSFORMER | RELAY |  |  |  | 120VAC OUTPUTS | TB1 |  | HT0001 | JBOX1 | 645CR |  | HCR1 | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | O:010/01 |  | SPARE
|  |  |  | O:010/02 |  | PILOT GAS VALVES | [5 empty] | TB1 |  | HT0001 | JBOX1 | D585SV |  | HSV1 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | O:010/03 |  | SPARE
|  |  |  | O:010/04 |  | SPARE
|  |  |  | O:010/05 |  | UPSTREAM GAS SHUTOFF | VALVE RELAY |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D573SV |  | HSV1 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | O:010/06 |  | DOWNSTREAM GAS SHUTOFF | VALVE RELAY |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D573SV |  | HSV1 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | O:010/07 |  | SPARE
|  |  |  | O:010/10 |  | SPARE
|  |  |  | O:010/11 |  | SPARE
|  |  |  | O:010/12 |  | SPARE
|  |  |  | O:010/13 |  | SPARE
|  |  |  | O:010/14 |  | SPARE
|  |  |  | O:010/15 |  | SPARE
|  |  |  | O:010/16 |  | SPARE
|  |  |  | O:010/17 |  | SPARE
1746-IO8 | 1 | 5 | 1 | O:011/00 | TB31 | SPARE |  |  |  |  | 4 OUT / 4 IN
|  |  |  | O:011/01 |  | GAS VENT VALVE (VGV) | [5 empty] | TB2 |  | HT0002 | JBOX2 | SV-VGV | GAS VENT No. 2 | HSV1 | FIELD | TB2 |  | HT0002 | JBOX2
|  |  |  | O:011/02 |  | SPARE
|  |  |  | O:011/03 |  | PURGE COMPLETE | [5 empty] | TB1 |  | HT0001 | JBOX1 | 102LT | PURGE COMPLETE | HLT1G | CAB5 | TB1 |  | HT0001 | JBOX1
|  |  |  | I:006/00 |  | BANK #2 FIBER | WASTE REMOVAL BLOWER | START HS1001BR | REMOTE |  |  | TB1 |  | HT0001 | JBOX1 | HS1001BR | START | HPB11 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:006/01 |  | BANK #2 FIBER | WASTE REMOVAL BLOWER | STOP HS1001BS |  |  |  | TB1 |  | HT0001 | JBOX1 | HS1001BS | STOP | HTS11 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:006/02 |  | TUB OUTLET TEMPERATURE | NOT LOW(ALARM) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D568TS | TUB OUTLET¦TEMP | HTS12 | FIELD | TB1 |  | HT0001 | JBOX1
|  |  |  | I:006/03 |  | TUB INLET TO HEATER FLOW | NOT LOW (TRIP) |  |  |  |  | TB1 |  | HT0001 | JBOX1 | D2150FS | TUB INLET | HFS11 | FIELD | TB1 |  | HT0001 | JBOX1